# (2026Aug FireSeal.docx)

# RECOMMENDED ENGINEERING SPECIFICATION FOR AssureFlex® FIRESEAL BELLOWS™

# PIPE FLOOR/WALL PENETRATION BELLOWS SEAL

## PART 1 GENERAL

1.01	SECTION INCLUDES

- AssureFlex FireSeal Bellows pipe penetration sealing system consisting of a flexible 300 series stainless steel bellows element extending around a penetrating pipe at a floor or wall opening. The bellows shall accommodate axial movement of the penetrating pipe while maintaining the firestop system.

  - Provide the appropriate seismic or non-seismic model for the application. Seismic models shall provide clearance around the penetrating pipe in accordance with NFPA 13 recommendations.

  - Provide end fittings suitable for attachment to the mating piping. End fittings may be carbon steel, 304 stainless steel, or 316 stainless steel, as specified.

  - Provide the appropriate nominal size from 2 inches through 12 inches.

1.02	MANUFACTURER

A.  Provide the appropriate AssureFlex FireSeal Bellows pipe penetration sealing system as manufactured by Flex-Hose Co., or approved equal.

PART 2 PRODUCTS

2.01 Pipe Floor/Wall Penetration Bellows Seal

## FireSeal Bellows assemblies shall be made in the USA.

- Bellows element shall be 300 series stainless steel.

- End fittings shall be carbon steel, 304 stainless steel, or 316 stainless steel, as specified for the mating piping.

- Base plate shall be carbon steel as standard. A 300 series stainless steel base plate shall be available as an option.

- Protective shroud shall be 300 series stainless steel and shall surround the bellows element to provide mechanical protection.

- The base plate shall be configured to attach to the floor or wall surrounding the pipe penetration.

- The flexible bellows shall accommodate axial expansion and contraction of the penetrating pipe while maintaining the fire seal.

- Seismic models shall provide clearance around the penetrating pipe in accordance with NFPA 13 recommendations. FireSeal Bellows shall be UL 1479 listed for penetration firestop applications.

- Fire-rated sealant shall be applied between the base plate and penetrating surface in accordance with the manufacturer's installation instructions. 3M™ CP 25WB+ fire-rated sealant is specified in the current installation instructions.

- The mating piping shall be independently supported so the FireSeal Bellows assembly does not carry the load of the piping system.

- The assembly shall require no routine maintenance other than periodic inspection for external damage and repainting of carbon steel surfaces as required.

- Product shall be covered by U.S. Patent No. 11,221,075 B2.